## Work instructions for the performance of hot work

## Must always be completed as a team before work is performed.

Hot work means work involving the use of machinery and equipment that generate sparks and heat that can cause a fire. 
Hot work includes the use of naked flames, hot air, and/or welding, cutting or grinding equipment.

## DETAILS of the work and SIGNATURES indicating that the form has been correctly competed and understood

| Description of the work: |
| --- |
| Workplace location (describe where the work is to be performed): |
| Date and time when the work starts: |  | Date and time when the work is completed: |
| Employer/client (person or company): | Mobile number: | Signature: |
| Person(s) or company performing the work: | Mobile number: | Signature: | Certificate no.: |
| Fire watch(es): | Mobile number: | Signature: | Certificate no.: |

## SAFETY REQUIREMENTS

The company or person performing the hot work undertakes to ensure that the work can be performed safely and in accordance with applicable laws and regulations. The hot work shall be finished well before the end of the working day.

| Before the work starts: |
| --- |
| 1  | Risks associated with combustible insulation in structures have been considered. |
| 2  | All openings in floors, walls and ceilings have been sealed. |
| 3  | Any hidden cavities (e.g. tiers of wooden joists, ventilation and extraction ducts, ducting or pipework) have been checked. |
| 4  | Flammable and combustible materials and liquids have been removed. |
| 5  | Protection has been provided for both combustible materials that cannot be moved and combustible building components or they have been dampened. |
| 6  | Approved fire extinguishing equipment (at least two 6 kg powder extinguishers with a minimum output of 34A 233B C) must be easily accessible. One portable fire extinguisher may be substituted with a fire hose with an internal diameter of at least 19 mm, with water turned on up to the nozzle. Is there a need for additional extinguishing equipment? Yes  No  |
| 7  | Fire detectors or detection loops have been disabled. |
| 8  | The specified fire watch(es) must be present during the work, during breaks and for at least one hour after work has finished. |
| 9  | Work equipment has been checked and in order. |
| 10  | The need for heightened readiness to be able to tackle an outbreak of fire has been assessed. |
| 11  | There are at least two emergency exits from the hazard area. |
| 12  | The emergency phone numbers and procedures for notifying of fires or accidents, and the address of the workplace are known. |

# Areas of high explosion risk (not relevant )

| This part of the instruction applies to areas, enclosed spaces or parts of same where there is a risk of explosion due to the presence of explosive substances or because the air is normally or may occasionally be mixed with flammable gases or fumes or combustible dust in such a proportion that the mixture can become explosive. The use of naked flames of any sort is forbidden, including welding, cutting and similar operations, without written permission from the owner or employer/client. | 13  | There is written permission from the owner or employer/client. |
| --- | --- | --- |
|  | 14  | Gas measurements have been taken. |
|  | 15  | Acetylene/oxygen cylinders have not been brought into the area. |
|  | 16  | Good ventilation has been provided. |

| Follow-up after completion of work: |
| --- |
| 17  | A follow-up check has been made to ensure there is no risk of a fire starting. |
| 18  | Fire detectors or detector loops have been re-activated by: ………………………………………………………... |
| 19  | Any gas cylinders have been placed close to an outer door/gateway so they can be easily moved to safety if a fire starts. |